## Calculation
CSTR with cell recycle example
Oxygen and MLVSS constrained design
Effluent COD < 25 mg/l, effluent ammonia < 1 mgNH4-N/l
Q (d) | S (mgCOD/l) | XBH*t (mgCOD*d/l) | XD*t (mgCOD*d/l) | XT*t (mgCOD*d/l) | YHobs (gCODx/gCODs) | WT (kgVSS/d) | XNHcells (mgN/l) | tmin (d) RO=1200 mgO2/l/d) | XTmax (mgVSS/l) | XBmax (mgVSS/l) | XDmax (mgVSS/l) | Vmin (m3) | new V(XT<2500 mgVSS/l) (m3) | new ROCOD (mgO2/l/d) | new t (days) | SNH (mgN/l) | XBA*t (mgCOD*d/l) | XBA (mgVSS/l) | new RONH (mgO2/l/d) | new ROtotal (mgO2/l/d) | VRO (kgO2/day)
| Ss | Xb*tau | Xd*tau | Xt*tau
0.5 | 26.2821 | 69.8437 | 0.34922 | 70.1929 | 0.62751 | 8541.7803 | 12.6347 | 0.069444 | 711.8246 | 708.2832 | 3.5414 | 5999.9189 | 1708.3561 | 1200 | 0.019773
1 | 8.8983 | 146.9572 | 1.4696 | 148.4268 | 0.61562 | 9031.0388 | 13.3584 | 0.077229 | 1353.4527 | 1340.0522 | 13.4005 | 6672.5927 | 3612.4155 | 1200 | 0.04181
2 | 3.9855 | 286.2714 | 5.7254 | 291.9968 | 0.59345 | 8883.2841 | 13.1399 | 0.083347 | 2467.1823 | 2418.8062 | 48.3761 | 7201.1573 | 7106.6273 | 1200 | 0.082253
3 | 2.6498 | 412.9673 | 12.389 | 425.3564 | 0.57322 | 8626.9459 | 12.7607 | 0.087971 | 3405.0759 | 3305.899 | 99.177 | 7600.6639 | 10352.3351 | 881.0376 | 0.11982 | -5.8571
4 | 2.027 | 529.009 | 21.1604 | 550.1694 | 0.55467 | 8368.7735 | 12.3788 | 0.092026 | 4210.1712 | 4048.2415 | 161.9297 | 7951.0054 | 13390.0376 | 712.5601 | 0.15498 | -63
5 | 1.6667 | 635.7333 | 31.7867 | 667.52 | 0.5376 | 8123.0603 | 12.0154 | 0.095691 | 4912.5201 | 4678.5906 | 233.9295 | 8267.712 | 16246.1206 | 610.6845 | 0.18803 | 3.6667 | 1.4235 | 1.0025 | 591.0274 | 1201.712 | 19523.1575
6 | 1.4317 | 734.2325 | 44.0539 | 778.2864 | 0.52185 | 7892.4819 | 11.6743 | 0.099045 | 5533.743 | 5220.5123 | 313.2307 | 8557.4794 | 18941.9566 | 542.1285 | 0.21924 | 1.8649 | 3.0241 | 2.1296 | 551.5803 | 1093.7088 | 20716.9846
7 | 1.2664 | 825.427 | 57.7799 | 883.2069 | 0.50726 | 7676.9694 | 11.3555 | 0.10213 | 6089.7919 | 5691.3943 | 398.3976 | 8824.4043 | 21495.5142 | 492.6277 | 0.24879 | 1.2857 | 5.9692 | 4.2037 | 502.5493 | 995.1769 | 21391.8401
8 | 1.1438 | 910.1027 | 72.8082 | 982.9109 | 0.49371 | 7475.6606 | 11.0577 | 0.10499 | 6592.6939 | 6104.3462 | 488.3477 | 9071.4487 | 23922.1138 | 455.0492 | 0.27688 | 1 | 8.7471 | 6.16 | 461.2027 | 916.2518 | 21918.6808
9 | 1.0492 | 988.9356 | 89.0042 | 1077.9398 | 0.4811 | 7287.4802 | 10.7794 | 0.10765 | 7051.6881 | 6469.4386 | 582.2495 | 9300.9391 | 26234.9287 | 425.43 | 0.30365 | 0.82979 | 11.3563 | 7.9974 | 427.2951 | 852.7251 | 22371.1834
10 | 0.97403 | 1062.5108 | 106.2511 | 1168.7619 | 0.46933 | 7111.34 | 10.5189 | 0.11012 | 7473.9897 | 6794.5361 | 679.4536 | 9514.7844 | 28445.3602 | 401.392 | 0.32923 | 0.71681 | 13.8069 | 9.7232 | 399.2756 | 800.6676 | 22775.279
11 | 0.91284 | 1131.3378 | 124.4472 | 1255.785 | 0.45832 | 6946.2114 | 10.2746 | 0.11244 | 7865.3148 | 7085.8692 | 779.4456 | 9714.5921 | 30563.3301 | 381.4215 | 0.35374 | 0.63636 | 16.1108 | 11.3457 | 375.8015 | 757.223 | 23143.2567
12 | 0.86207 | 1195.8621 | 143.5034 | 1339.3655 | 0.448 | 6791.1491 | 10.0452 | 0.1146 | 8230.2511 | 7348.4385 | 881.8126 | 9901.7379 | 32597.5157 | 364.5089 | 0.37729 | 0.57616 | 18.28 | 12.8733 | 355.8578 | 720.3668 | 23482.1668
13 | 0.81927 | 1256.475 | 163.3417 | 1419.8167 | 0.4383 | 6645.296 | 9.8295 | 0.11664 | 8572.5227 | 7586.3033 | 986.2194 | 10077.4126 | 34555.5395 | 349.9553 | 0.39995 | 0.52941 | 20.3253 | 14.3136 | 338.6931 | 688.6485 | 23796.6193
14 | 0.78269 | 1313.5218 | 183.8931 | 1497.4149 | 0.42918 | 6507.8796 | 9.6262 | 0.11855 | 8895.1848 | 7802.7937 | 1092.3911 | 10242.6556 | 36444.1256 | 337.2611 | 0.42181 | 0.49206 | 22.2567 | 15.6737 | 323.7484 | 661.0096 | 24089.9154
15 | 0.75107 | 1367.3084 | 205.0963 | 1572.4047 | 0.42057 | 6378.2048 | 9.4344 | 0.12035 | 9200.7667 | 8000.6667 | 1200.1 | 10398.3804 | 38269.2289 | 326.0598 | 0.44293 | 0.46154 | 24.0832 | 16.96 | 310.6025 | 636.6623 | 24364.5739
16 | 0.72347 | 1418.1065 | 226.897 | 1645.0035 | 0.41244 | 6255.6471 | 9.2531 | 0.12205 | 9491.381 | 8182.225 | 1309.156 | 10545.3942 | 40036.1416 | 316.0762 | 0.46338 | 0.43612 | 25.813 | 18.1782 | 298.9332 | 615.0094 | 24622.6049
17 | 0.69917 | 1466.1584 | 249.2469 | 1715.4053 | 0.40476 | 6139.6446 | 9.0816 | 0.12366 | 9768.8053 | 8349.4063 | 1419.3991 | 10684.4138 | 41749.5833 | 307.1 | 0.48321 | 0.41463 | 27.4534 | 19.3334 | 288.4907 | 595.5907 | 24865.6642
18 | 0.6776 | 1511.6811 | 272.1026 | 1783.7836 | 0.39747 | 6029.6912 | 8.9189 | 0.12519 | 10034.5469 | 8503.8533 | 1530.6936 | 10816.078 | 43413.7767 | 298.9672 | 0.50247 | 0.39623 | 29.0111 | 20.4304 | 279.0785 | 578.0457 | 25095.1473
19 | 0.65834 | 1554.869 | 295.4251 | 1850.2941 | 0.39056 | 5925.3304 | 8.7646 | 0.12663 | 10289.8915 | 8646.9676 | 1642.9239 | 10940.9586 | 45032.5109 | 291.5483 | 0.52121 | 0.38028 | 30.4922 | 21.4734 | 270.5401 | 562.0884 | 25312.2514
20 | 0.64103 | 1595.8974 | 319.1795 | 1915.0769 | 0.384 | 5826.1495 | 8.6178 | 0.128 | 10535.9429 | 8779.9524 | 1755.9905 | 11059.5692 | 46609.1961 | 284.7396 | 0.53946 | 0.36634 | 31.902 | 22.4662 | 262.7493 | 547.4889 | 25518.0165
21 | 0.62538 | 1634.9243 | 343.3341 | 1978.2584 | 0.37776 | 5731.775 | 8.4783 | 0.12931 | 10773.6542 | 8903.8464 | 1869.8077 | 11172.3722 | 48146.9096 | 278.4571 | 0.55726 | 0.35404 | 33.2456 | 23.4124 | 255.6033 | 534.0604 | 25713.3555
22 | 0.61118 | 1672.0927 | 367.8604 | 2039.9531 | 0.37181 | 5641.8677 | 8.3453 | 0.13055 | 11003.8521 | 9019.5509 | 1984.3012 | 11279.7853 | 49648.4355 | 272.6318 | 0.57463 | 0.34311 | 34.5274 | 24.3151 | 249.0176 | 521.6494 | 25899.0764
23 | 0.59822 | 1707.5322 | 392.7324 | 2100.2646 | 0.36614 | 5556.1194 | 8.2184 | 0.13174 | 11227.2579 | 9127.8519 | 2099.4059 | 11382.1869 | 51116.2989 | 267.2068 | 0.59162 | 0.33333 | 35.7517 | 25.1772 | 242.922 | 510.1289 | 26075.8989
24 | 0.58635 | 1741.3607 | 417.9266 | 2159.2873 | 0.36073 | 5474.2495 | 8.0973 | 0.13287 | 11444.5032 | 9229.4381 | 2215.0651 | 11479.9206 | 52552.7952 | 262.1346 | 0.60825 | 0.32454 | 36.9221 | 26.0015 | 237.2578 | 499.3924 | 26244.4679
25 | 0.57545 | 1773.6857 | 443.4214 | 2217.1071 | 0.35556 | 5396.0016 | 7.9816 | 0.13395 | 11656.1438 | 9324.915 | 2331.2288 | 11573.2992 | 53960.0158 | 257.375 | 0.62454 | 0.31658 | 38.0422 | 26.7903 | 231.9756 | 489.3506 | 26405.3638
excluded values for Q
for constraints, X=2500 mgVSS/l, ROtotal < 1200 mgO2/l/d,
design space is driven by effluent ammonia < 1 mgN/l
for minimum volume, select Q = 8 days, V = 24,000 m3,
ROtotal = 916 mgO2/l/d, t = 7 hr (0.28 d)
sludge wasting rate is 7.5 metric tons VSS/day

## Graphs
Graphs of the effects of Q on Process Components in CSTR with Cell Recycle using Example Data